## Cover-Page
INSTRUMENT I/O LIST
[6 empty] | CLIENT: | PT Marunda Tank Terminal | CLIENT DOC NO. | 24E11-J1-LI-1002
[8 empty] | JOB NO. | 24E11
[8 empty] | PAGE NO. | 1 OF 18
0 | 23-06-2025 | APPROVED FOR DESIGN | WYJ | LXL | APM | DESIGN ENGINEER: |  | PROJECT TITLE | PT Marunda Tank Terminal Storage Project
A | 23-01-2025 | ISSUED FOR APPROVAL | WYJ | LXL | APM |  | Abraham International Process Engineering Corp Pte. Ltd
REV | DATE | DESCRIPTION | PREPARED BY | CHECKED BY | APPROVED BY |  |  | LOCATION | Tanah Abang, Jakarta Pusat, Indonesia

## IO Summary
Instrument I/O Summary
S/N | Area | DI | DO | AI | AO | PI | Remarks
1 | TF-01 | 112 | 48 | 16 | 0 | 0
2 | PUMP STATION | 20 | 14 | 15 | 6 | 0
3 | JETTY | 4 | 2 | 1 | 0 | 0
4 | TLB | 48 | 16 | 33 | 8 | 0
5 | HOT WATER SYS. | 22 | 0 | 4 | 0 | 0
6 | POTABLE WATER SYS. | 9 | 0 | 3 | 0 | 0
7 | PLANT AIR SYS. | 6 | 0 | 2 | 0 | 0
8 | 10% Feed Margin | 244 | 88 | 82 | 16 | 0
9 | Including 20% Spare | 293 | 106 | 99 | 20 | 0
This is preliminary IO list and will be finalized during detail design.

## TF
S/N | Revision No. | DCS Tag Number | Instrument Tag No. | Signal Description | Equipment | P & ID Dwg No. | P&ID Revision No. | IO Type | Signal Type | Power | Zero Stauts | One Stauts | Alarm Setting |  |  |  | Range |  | Unit | RIO Panel No. | Slot Number | Channel Number | Remarks
[13 empty] | LL | L | H | HH | 0% | 100% | [5 empty] | used | spare
INSTRUMENT I/O FOR TANK FARM 01
1 | A | 01LSHH0101 | 01-LS-0101 | T-101 Level Switch | T-101 | 24E11-P1-PI-1002 | A | DI | Dry Contact | -
2 | A | 01LSHH0201 | 01-LS-0201 | T-102 Level Switch | T-102 | 24E11-P1-PI-1002 | A | DI | Dry Contact | -
3 | A | 01LSHH0301 | 01-LS-0301 | T-103 Level Switch | T-103 | 24E11-P1-PI-1002 | A | DI | Dry Contact | -
4 | A | 01LSHH0401 | 01-LS-0401 | T-104 Level Switch | T-104 | 24E11-P1-PI-1002 | A | DI | Dry Contact | -
5 | A | 01LSHH0501 | 01-LS-0501 | T-105 Level Switch | T-105 | 24E11-P1-PI-1001 | A | DI | Dry Contact | -
6 | A | 01LSHH0601 | 01-LS-0601 | T-106 Level Switch | T-106 | 24E11-P1-PI-1001 | A | DI | Dry Contact | -
7 | A | 01LSHH0701 | 01-LS-0701 | T-107 Level Switch | T-107 | 24E11-P1-PI-1001 | A | DI | Dry Contact | -
8 | A | 01LSHH0801 | 01-LS-0801 | T-108 Level Switch | T-108 | 24E11-P1-PI-1001 | A | DI | Dry Contact | -
9 | A | 01LALL0101 | 01-LS-0101 | T-101 Radar Gauge Switch Output | T-101 | 24E11-P1-PI-1002 | A | DI | Dry Contact | -
10 | A | 01LALL0201 | 01-LS-0201 | T-102 Radar Gauge Switch Output | T-102 | 24E11-P1-PI-1002 | A | DI | Dry Contact | -
11 | A | 01LALL0301 | 01-LS-0301 | T-103 Radar Gauge Switch Output | T-103 | 24E11-P1-PI-1002 | A | DI | Dry Contact | -
12 | A | 01LALL0401 | 01-LS-0401 | T-104 Radar Gauge Switch Output | T-104 | 24E11-P1-PI-1002 | A | DI | Dry Contact | -
13 | A | 01LALL0501 | 01-LS-0501 | T-105 Radar Gauge Switch Output | T-105 | 24E11-P1-PI-1001 | A | DI | Dry Contact | -
14 | A | 01LALL0601 | 01-LS-0601 | T-106 Radar Gauge Switch Output | T-106 | 24E11-P1-PI-1001 | A | DI | Dry Contact | -
15 | A | 01LALL0701 | 01-LS-0701 | T-107 Radar Gauge Switch Output | T-107 | 24E11-P1-PI-1001 | A | DI | Dry Contact | -
16 | A | 01LALL0801 | 01-LS-0801 | T-108 Radar Gauge Switch Output | T-108 | 24E11-P1-PI-1001 | A | DI | Dry Contact | -
17 | A | 01TI0102 | 01-TT-0102 | T-101 Temperature | T-101 | 24E11-P1-PI-1002 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | ℃
18 | A | 01TI0202 | 01-TT-0202 | T-102 Temperature | T-102 | 24E11-P1-PI-1002 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | ℃
19 | A | 01TI0302 | 01-TT-0302 | T-103 Temperature | T-103 | 24E11-P1-PI-1002 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | ℃
20 | A | 01TI0402 | 01-TT-0402 | T-104 Temperature | T-104 | 24E11-P1-PI-1002 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | ℃
21 | A | 01TI0502 | 01-TT-0502 | T-105 Temperature | T-105 | 24E11-P1-PI-1001 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | ℃
22 | A | 01TI0602 | 01-TT-0602 | T-106 Temperature | T-106 | 24E11-P1-PI-1001 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | ℃
23 | A | 01TI0702 | 01-TT-0702 | T-107 Temperature | T-107 | 24E11-P1-PI-1001 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | ℃
24 | A | 01TI0802 | 01-TT-0802 | T-108 Temperature | T-108 | 24E11-P1-PI-1001 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | ℃
25 | A | 01ZLL0101 | 01-ZSL-0101 | 01-MOV-0101 Fully Closed | 01-MOV-0101 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Closed
26 | A | 01ZLH0101 | 01-ZSH-0101 | 01-MOV-0101 Fully Open | 01-MOV-0101 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Open
27 | A | 01XS0101 | 01-HS-0101 | Local/Remote/Off Switch | 01-MOV-0101 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | Remote | Local/Off
28 | 0 | 01XA0101 | 01-XA-0101 | Fault | 01-MOV-0101 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Alarm
29 | A | 01HSC0101 | 01-MOV-0101 | 01-MOV-0101 Open Command | 01-MOV-0101 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Open
30 | A | 01HSO0101 | 01-MOV-0101 | 01-MOV-0101 Close Command | 01-MOV-0101 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Close
31 | A | 01ZLL0102 | 01-ZSL-0102 | 01-MOV-0102 Fully Closed | 01-MOV-0102 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Closed
32 | A | 01ZLH0102 | 01-ZSH-0102 | 01-MOV-0102 Fully Open | 01-MOV-0102 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Open
33 | A | 01XS0102 | 01-HS-0102 | Local/Remote/Off Switch | 01-MOV-0102 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | Remote | Local/Off
34 | 0 | 01XA0102 | 01-XA-0102 | Fault | 01-MOV-0102 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Alarm
35 | A | 01HSC0102 | 01-MOV-0102 | 01-MOV-0102 Open Command | 01-MOV-0102 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Open
36 | A | 01HSO0102 | 01-MOV-0102 | 01-MOV-0102 Close Command | 01-MOV-0102 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Close
37 | A | 01ZI0102 | 01-ZT-0102 | 01-MOV-0102 Opening Position Feedback | 01-MOV-0102 | 24E11-P1-PI-1002 | A | AI | 4~20mA | - | - | - |  |  |  |  | 0 | 100 | %
38 | A | 01ZLL0103 | 01-ZSL-0103 | 01-MOV-0103 Fully Closed | 01-MOV-0103 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Closed
39 | A | 01ZLH0103 | 01-ZSH-0103 | 01-MOV-0103 Fully Open | 01-MOV-0103 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Open
40 | A | 01XS0103 | 01-HS-0103 | Local/Remote/Off Switch | 01-MOV-0103 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | Remote | Local/Off
41 | 0 | 01XA0103 | 01-XA-0103 | Fault | 01-MOV-0103 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Alarm
42 | A | 01HSC0103 | 01-MOV-0103 | 01-MOV-0103 Open Command | 01-MOV-0103 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Open
43 | A | 01HSO0103 | 01-MOV-0103 | 01-MOV-0103 Close Command | 01-MOV-0103 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Close
44 | A | 01ZLL0201 | 01-ZSL-0201 | 01-MOV-0201 Fully Closed | 01-MOV-0201 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Closed
45 | A | 01ZLH0201 | 01-ZSH-0201 | 01-MOV-0201 Fully Open | 01-MOV-0201 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Open
46 | A | 01XS0201 | 01-HS-0201 | Local/Remote/Off Switch | 01-MOV-0201 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | Remote | Local/Off
47 | 0 | 01XA0201 | 01-XA-0201 | Fault | 01-MOV-0201 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Alarm
48 | A | 01HSC0201 | 01-MOV-0201 | 01-MOV-0201 Open Command | 01-MOV-0201 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Open
49 | A | 01HSO0201 | 01-MOV-0201 | 01-MOV-0201 Close Command | 01-MOV-0201 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Close
50 | A | 01ZLL0202 | 01-ZSL-0202 | 01-MOV-0202 Fully Closed | 01-MOV-0202 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Closed
51 | A | 01ZLH0202 | 01-ZSH-0202 | 01-MOV-0202 Fully Open | 01-MOV-0202 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Open
52 | A | 01XS0202 | 01-HS-0202 | Local/Remote/Off Switch | 01-MOV-0202 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | Remote | Local/Off
53 | 0 | 01XA0202 | 01-XA-0202 | Fault | 01-MOV-0202 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Alarm
54 | A | 01HSC0202 | 01-MOV-0202 | 01-MOV-0202 Open Command | 01-MOV-0202 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Open
55 | A | 01HSO0202 | 01-MOV-0202 | 01-MOV-0202 Close Command | 01-MOV-0202 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Close
56 | A | 01ZI0202 | 01-ZT-0202 | 01-MOV-0202 Opening Position Feedback | 01-MOV-0202 | 24E11-P1-PI-1002 | A | AI | 4~20mA | - | - | - |  |  |  |  | 0 | 100 | %
57 | A | 01ZLL0203 | 01-ZSL-0203 | 01-MOV-0203 Fully Closed | 01-MOV-0203 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Closed
58 | A | 01ZLH0203 | 01-ZSH-0203 | 01-MOV-0203 Fully Open | 01-MOV-0203 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Open
59 | A | 01XS0203 | 01-HS-0203 | Local/Remote/Off Switch | 01-MOV-0203 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | Remote | Local/Off
60 | 0 | 01XA0203 | 01-XA-0203 | Fault | 01-MOV-0203 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Alarm
61 | A | 01HSC0203 | 01-MOV-0203 | 01-MOV-0203 Open Command | 01-MOV-0203 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Open
62 | A | 01HSO0203 | 01-MOV-0203 | 01-MOV-0203 Close Command | 01-MOV-0203 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Close
63 | A | 01ZLL0301 | 01-ZSL-0301 | 01-MOV-0301 Fully Closed | 01-MOV-0301 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Closed
64 | A | 01ZLH0301 | 01-ZSH-0301 | 01-MOV-0301 Fully Open | 01-MOV-0301 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Open
65 | A | 01XS0301 | 01-HS-0301 | Local/Remote/Off Switch | 01-MOV-0301 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | Remote | Local/Off
66 | 0 | 01XA0301 | 01-XA-0301 | Fault | 01-MOV-0301 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Alarm
67 | A | 01HSC0301 | 01-MOV-0301 | 01-MOV-0301 Open Command | 01-MOV-0301 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Open
68 | A | 01HSO0301 | 01-MOV-0301 | 01-MOV-0301 Close Command | 01-MOV-0301 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Close
69 | A | 01ZLL0302 | 01-ZSL-0302 | 01-MOV-0302 Fully Closed | 01-MOV-0302 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Closed
70 | A | 01ZLH0302 | 01-ZSH-0302 | 01-MOV-0302 Fully Open | 01-MOV-0302 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Open
71 | A | 01XS0302 | 01-HS-0302 | Local/Remote/Off Switch | 01-MOV-0302 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | Remote | Local/Off
72 | 0 | 01XA0302 | 01-XA-0302 | Fault | 01-MOV-0302 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Alarm
73 | A | 01HSC0302 | 01-MOV-0302 | 01-MOV-0302 Open Command | 01-MOV-0302 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Open
74 | A | 01HSO0302 | 01-MOV-0302 | 01-MOV-0302 Close Command | 01-MOV-0302 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Close
75 | A | 01ZI0302 | 01-ZT-0302 | 01-MOV-0302 Opening Position Feedback | 01-MOV-0302 | 24E11-P1-PI-1002 | A | AI | 4~20mA | - | - | - |  |  |  |  | 0 | 100 | %
76 | A | 01ZLL0303 | 01-ZSL-0303 | 01-MOV-0303 Fully Closed | 01-MOV-0303 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Closed
77 | A | 01ZLH0303 | 01-ZSH-0303 | 01-MOV-0303 Fully Open | 01-MOV-0303 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Open
78 | A | 01XS0303 | 01-HS-0303 | Local/Remote/Off Switch | 01-MOV-0303 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | Remote | Local/Off
79 | 0 | 01XA0303 | 01-XA-0303 | Fault | 01-MOV-0303 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Alarm
80 | A | 01HSC0303 | 01-MOV-0303 | 01-MOV-0303 Open Command | 01-MOV-0303 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Open
81 | A | 01HSO0303 | 01-MOV-0303 | 01-MOV-0303 Close Command | 01-MOV-0303 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Close
82 | A | 01ZLL0401 | 01-ZSL-0401 | 01-MOV-0401 Fully Closed | 01-MOV-0401 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Closed
83 | A | 01ZLH0401 | 01-ZSH-0401 | 01-MOV-0401 Fully Open | 01-MOV-0401 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Open
84 | A | 01XS0401 | 01-HS-0401 | Local/Remote/Off Switch | 01-MOV-0401 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | Remote | Local/Off
85 | 0 | 01XA0401 | 01-XA-0401 | Fault | 01-MOV-0401 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Alarm
86 | A | 01HSC0401 | 01-MOV-0401 | 01-MOV-0401 Open Command | 01-MOV-0401 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Open
87 | A | 01HSO0401 | 01-MOV-0401 | 01-MOV-0401 Close Command | 01-MOV-0401 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Close
88 | A | 01ZLL0402 | 01-ZSL-0402 | 01-MOV-0402 Fully Closed | 01-MOV-0402 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Closed
89 | A | 01ZLH0402 | 01-ZSH-0402 | 01-MOV-0402 Fully Open | 01-MOV-0402 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Open
90 | A | 01XS0402 | 01-HS-0402 | Local/Remote/Off Switch | 01-MOV-0402 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | Remote | Local/Off
91 | 0 | 01XA0402 | 01-XA-0402 | Fault | 01-MOV-0402 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Alarm
92 | A | 01HSC0402 | 01-MOV-0402 | 01-MOV-0402 Close Command | 01-MOV-0402 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Open
93 | A | 01HSO0402 | 01-MOV-0402 | 01-MOV-0402 Open Command | 01-MOV-0402 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Close
94 | A | 01ZI0402 | 01-ZT-0402 | 01-MOV-0402 Opening Position Feedback | 01-MOV-0402 | 24E11-P1-PI-1002 | A | AI | 4~20mA | - | - | - |  |  |  |  | 0 | 100 | %
95 | A | 01ZLL0403 | 01-ZSL-0403 | 01-MOV-0403 Fully Closed | 01-MOV-0403 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Closed
96 | A | 01ZLH0403 | 01-ZSH-0403 | 01-MOV-0403 Fully Open | 01-MOV-0403 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Open
97 | A | 01XS0403 | 01-HS-0403 | Local/Remote/Off Switch | 01-MOV-0403 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | Remote | Local/Off
98 | 0 | 01XA0403 | 01-XA-0403 | Fault | 01-MOV-0403 | 24E11-P1-PI-1002 | A | DI | Dry Contact | - | - | Alarm
99 | A | 01HSC0403 | 01-MOV-0403 | 01-MOV-0403 Close Command | 01-MOV-0403 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Open
100 | A | 01HSO0403 | 01-MOV-0403 | 01-MOV-0403 Open Command | 01-MOV-0403 | 24E11-P1-PI-1002 | A | DO | Dry Contact | - | - | Close
101 | A | 01ZLL0501 | 01-ZSL-0501 | 01-MOV-0501 Fully Closed | 01-MOV-0501 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Closed
102 | A | 01ZLH0501 | 01-ZSH-0501 | 01-MOV-0501 Fully Open | 01-MOV-0501 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Open
103 | A | 01XS0501 | 01-HS-0501 | Local/Remote/Off Switch | 01-MOV-0501 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | Remote | Local/Off
104 | 0 | 01XA0501 | 01-XA-0501 | Fault | 01-MOV-0501 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Alarm
105 | A | 01HSC0501 | 01-MOV-0501 | 01-MOV-0501 Close Command | 01-MOV-0501 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Open
106 | A | 01HSO0501 | 01-MOV-0501 | 01-MOV-0501 Open Command | 01-MOV-0501 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Close
107 | A | 01ZLL0502 | 01-ZSL-0502 | 01-MOV-0502 Fully Closed | 01-MOV-0502 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Closed
108 | A | 01ZLH0502 | 01-ZSH-0502 | 01-MOV-0502 Fully Open | 01-MOV-0502 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Open
109 | A | 01XS0502 | 01-HS-0502 | Local/Remote/Off Switch | 01-MOV-0502 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | Remote | Local/Off
110 | 0 | 01XA0502 | 01-XA-0502 | Fault | 01-MOV-0502 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Alarm
111 | A | 01HSC0502 | 01-MOV-0502 | 01-MOV-0502 Close Command | 01-MOV-0502 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Open
112 | A | 01HSO0502 | 01-MOV-0502 | 01-MOV-0502 Open Command | 01-MOV-0502 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Close
113 | A | 01ZI0502 | 01-ZT-0502 | 01-MOV-0502 Opening Position Feedback | 01-MOV-0502 | 24E11-P1-PI-1001 | A | AI | 4~20mA | - | - | - |  |  |  |  | 0 | 100 | %
114 | A | 01ZLL0503 | 01-ZSL-0503 | 01-MOV-0503 Fully Closed | 01-MOV-0503 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Closed
115 | A | 01ZLH0503 | 01-ZSH-0503 | 01-MOV-0503 Fully Open | 01-MOV-0503 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Open
116 | A | 01XS0503 | 01-HS-0503 | Local/Remote/Off Switch | 01-MOV-0503 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | Remote | Local/Off
117 | 0 | 01XA0503 | 01-XA-0503 | Fault | 01-MOV-0503 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Alarm
118 | A | 01HSC0503 | 01-MOV-0503 | 01-MOV-0503 Close Command | 01-MOV-0503 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Open
119 | A | 01HSO0503 | 01-MOV-0503 | 01-MOV-0503 Open Command | 01-MOV-0503 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Close
120 | A | 01ZLL0601 | 01-ZSL-0601 | 01-MOV-0601 Fully Closed | 01-MOV-0601 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Closed
121 | A | 01ZLH0601 | 01-ZSH-0601 | 01-MOV-0601 Fully Open | 01-MOV-0601 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Open
122 | A | 01XS0601 | 01-HS-0601 | Local/Remote/Off Switch | 01-MOV-0601 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | Remote | Local/Off
123 | 0 | 01XA0601 | 01-XA-0601 | Fault | 01-MOV-0601 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Alarm
124 | A | 01HSC0601 | 01-MOV-0601 | 01-MOV-0601 Close Command | 01-MOV-0601 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Open
125 | A | 01HSO0601 | 01-MOV-0601 | 01-MOV-0601 Open Command | 01-MOV-0601 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Close
126 | A | 01ZLL0602 | 01-ZSL-0602 | 01-MOV-0602 Fully Closed | 01-MOV-0602 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Closed
127 | A | 01ZLH0602 | 01-ZSH-0602 | 01-MOV-0602 Fully Open | 01-MOV-0602 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Open
128 | A | 01XS0602 | 01-HS-0602 | Local/Remote/Off Switch | 01-MOV-0602 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | Remote | Local/Off
129 | 0 | 01XA0602 | 01-XA-0602 | Fault | 01-MOV-0602 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Alarm
130 | A | 01HSC0602 | 01-MOV-0602 | 01-MOV-0602 Close Command | 01-MOV-0602 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Open
131 | A | 01HSO0602 | 01-MOV-0602 | 01-MOV-0602 Open Command | 01-MOV-0602 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Close
132 | A | 01ZI0602 | 01-ZT-0602 | 01-MOV-0602 Opening Position Feedback | 01-MOV-0602 | 24E11-P1-PI-1001 | A | AI | 4~20mA | - | - | - |  |  |  |  | 0 | 100 | %
133 | A | 01ZLL0603 | 01-ZSL-0603 | 01-MOV-0603 Fully Closed | 01-MOV-0603 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Closed
134 | A | 01ZLH0603 | 01-ZSH-0603 | 01-MOV-0603 Fully Open | 01-MOV-0603 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Open
135 | A | 01XS0603 | 01-HS-0603 | Local/Remote/Off Switch | 01-MOV-0603 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | Remote | Local/Off
136 | 0 | 01XA0603 | 01-XA-0603 | Fault | 01-MOV-0603 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Alarm
137 | A | 01HSC0603 | 01-MOV-0603 | 01-MOV-0603 Close Command | 01-MOV-0603 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Open
138 | A | 01HSO0603 | 01-MOV-0603 | 01-MOV-0603 Open Command | 01-MOV-0603 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Close
139 | A | 01ZLL0701 | 01-ZSL-0701 | 01-MOV-0701 Fully Closed | 01-MOV-0701 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Closed
140 | A | 01ZLH0701 | 01-ZSH-0701 | 01-MOV-0701 Fully Open | 01-MOV-0701 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Open
141 | A | 01XS0701 | 01-HS-0701 | Local/Remote/Off Switch | 01-MOV-0701 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | Remote | Local/Off
142 | 0 | 01XA0701 | 01-XA-0701 | Fault | 01-MOV-0701 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Alarm
143 | A | 01HSC0701 | 01-MOV-0701 | 01-MOV-0701 Close Command | 01-MOV-0701 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Open
144 | A | 01HSO0701 | 01-MOV-0701 | 01-MOV-0701 Open Command | 01-MOV-0701 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Close
145 | A | 01ZLL0702 | 01-ZSL-0702 | 01-MOV-0702 Fully Closed | 01-MOV-0702 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Closed
146 | A | 01ZLH0702 | 01-ZSH-0702 | 01-MOV-0702 Fully Open | 01-MOV-0702 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Open
147 | A | 01XS0702 | 01-HS-0702 | Local/Remote/Off Switch | 01-MOV-0702 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | Remote | Local/Off
148 | 0 | 01XA0702 | 01-XA-0702 | Fault | 01-MOV-0702 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Alarm
149 | A | 01HSC0702 | 01-MOV-0702 | 01-MOV-0702 Close Command | 01-MOV-0702 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Open
150 | A | 01HSO0702 | 01-MOV-0702 | 01-MOV-0702 Open Command | 01-MOV-0702 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Close
151 | A | 01ZI0702 | 01-ZT-0702 | 01-MOV-0702 Opening Position Feedback | 01-MOV-0702 | 24E11-P1-PI-1001 | A | AI | 4~20mA | - | - | - |  |  |  |  | 0 | 100 | %
152 | A | 01ZLL0703 | 01-ZSL-0703 | 01-MOV-0703 Fully Closed | 01-MOV-0703 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Closed
153 | A | 01ZLH0703 | 01-ZSH-0703 | 01-MOV-0703 Fully Open | 01-MOV-0703 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Open
154 | A | 01XS0703 | 01-HS-0703 | Local/Remote/Off Switch | 01-MOV-0703 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | Remote | Local/Off
155 | 0 | 01XA0702 | 01-XA-0703 | Fault | 01-MOV-0703 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Alarm
156 | A | 01HSC0703 | 01-MOV-0703 | 01-MOV-0703 Close Command | 01-MOV-0703 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Open
157 | A | 01HSO0703 | 01-MOV-0703 | 01-MOV-0703 Open Command | 01-MOV-0703 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Close
158 | A | 01ZLL0801 | 01-ZSL-0801 | 01-MOV-0801 Fully Closed | 01-MOV-0801 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Closed
159 | A | 01ZLH0801 | 01-ZSH-0801 | 01-MOV-0801 Fully Open | 01-MOV-0801 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Open
160 | A | 01XS0801 | 01-HS-0801 | Local/Remote/Off Switch | 01-MOV-0801 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | Remote | Local/Off
161 | 0 | 01XA0801 | 01-XA-0801 | Fault | 01-MOV-0801 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Alarm
162 | A | 01HSC0801 | 01-MOV-0801 | 01-MOV-0801 Close Command | 01-MOV-0801 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Open
163 | A | 01HSO0801 | 01-MOV-0801 | 01-MOV-0801 Open Command | 01-MOV-0801 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Close
164 | A | 01ZLL0802 | 01-ZSL-0802 | 01-MOV-0802 Fully Closed | 01-MOV-0802 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Closed
165 | A | 01ZLH0802 | 01-ZSH-0802 | 01-MOV-0802 Fully Open | 01-MOV-0802 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Open
166 | A | 01XS0802 | 01-HS-0802 | Local/Remote/Off Switch | 01-MOV-0802 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | Remote | Local/Off
167 | 0 | 01XA0802 | 01-XA-0802 | Fault | 01-MOV-0802 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Alarm
168 | A | 01HSC0802 | 01-MOV-0802 | 01-MOV-0802 Close Command | 01-MOV-0802 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Open
169 | A | 01HSO0802 | 01-MOV-0802 | 01-MOV-0802 Open Command | 01-MOV-0802 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Close
170 | A | 01ZI0802 | 01-ZT-0802 | 01-MOV-0802 Opening Position Feedback | 01-MOV-0802 | 24E11-P1-PI-1001 | A | AI | 4~20mA | - | - | - |  |  |  |  | 0 | 100 | %
171 | A | 01ZLL0803 | 01-ZSL-0803 | 01-MOV-0803 Fully Closed | 01-MOV-0803 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Closed
172 | A | 01ZLH0803 | 01-ZSH-0803 | 01-MOV-0803 Fully Open | 01-MOV-0803 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Open
173 | A | 01XS0803 | 01-HS-0803 | Local/Remote/Off Switch | 01-MOV-0803 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | Remote | Local/Off
174 | 0 | 01XA0803 | 01-XA-0803 | Fault | 01-MOV-0803 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Alarm
175 | A | 01HSC0803 | 01-MOV-0803 | 01-MOV-0803 Close Command | 01-MOV-0803 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Open
176 | A | 01HSO0803 | 01-MOV-0803 | 01-MOV-0803 Open Command | 01-MOV-0803 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Close
0

## PUMPS
S/N | Revision No. | DCS Tag Number | Instrument Tag No. | Signal Description | Equipment | P & ID Dwg No. | P&ID Revision No. | IO Type | Signal Type | Power | Zero Stauts | One Stauts | Alarm Setting |  |  |  | Range |  | Unit | RIO Panel No. | Slot Number | Channel Number | Remarks
[13 empty] | LL | L | H | HH | 0% | 100% | [5 empty] | used | spare
INSTRUMENT I/O FOR PUMP STATION 01
1 | A | 01TI0001 | 01-TT-0001 | P-101 Temperature | P-101 | 24E11-P1-PI-1004 | A | AI | 4~20mA | Loop Powered | - | -
2 | A | 01TI0002 | 01-TT-0002 | P-102 Temperature | P-102 | 24E11-P1-PI-1004 | A | AI | 4~20mA | Loop Powered | - | -
3 | A | 01TI0003 | 01-TT-0003 | P-103 Temperature | P-103 | 24E11-P1-PI-1004 | A | AI | 4~20mA | Loop Powered | - | -
4 | A | 01TI0004 | 01-TT-0004 | P-104 Temperature | P-104 | 24E11-P1-PI-1004 | A | AI | 4~20mA | Loop Powered | - | -
5 | A | 01TI0005 | 01-TT-0005 | P-105 Temperature | P-105 | 24E11-P1-PI-1004 | A | AI | 4~20mA | Loop Powered | - | -
6 | A | 01TI0006 | 01-TT-0006 | P-106 Temperature | P-106 | 24E11-P1-PI-1004 | A | AI | 4~20mA | Loop Powered | - | -
7 | A | 01TI0007 | 01-TT-0007 | P-107 Temperature | P-107 | 24E11-P1-PI-1004 | A | AI | 4~20mA | Loop Powered | - | -
8 | A | 04TI0001 | 04-TT-0001 | P-401 Temperature | P-401 | 24E11-P1-PI-1005 | A | AI | 4~20mA | Loop Powered | - | -
9 | A | 01LSL0001 | 01-LSL-0001 | P-101 Suction Low Level Protection | P-101 | 24E11-P1-PI-1004 | A | DI | Dry Contact | 24VDC | - | L Level
10 | A | 01LSL0002 | 01-LSL-0002 | P-102 Suction Low Level Protection | P-102 | 24E11-P1-PI-1004 | A | DI | Dry Contact | 24VDC | - | L Level
11 | A | 01LSL0003 | 01-LSL-0003 | P-103 Suction Low Level Protection | P-103 | 24E11-P1-PI-1004 | A | DI | Dry Contact | 24VDC | - | L Level
12 | A | 01LSL0004 | 01-LSL-0004 | P-104 Suction Low Level Protection | P-104 | 24E11-P1-PI-1004 | A | DI | Dry Contact | 24VDC | - | L Level
13 | A | 01LSL0005 | 01-LSL-0005 | P-105 Suction Low Level Protection | P-105 | 24E11-P1-PI-1004 | A | DI | Dry Contact | 24VDC | - | L Level
14 | A | 01LSL0006 | 01-LSL-0006 | P-106 Suction Low Level Protection | P-106 | 24E11-P1-PI-1004 | A | DI | Dry Contact | 24VDC | - | L Level
15 | A | 01PI0001 | 01-PT-0001 | P-101 Discharge Pressure | P-101 | 24E11-P1-PI-1004 | A | AI | 4~20mA | Loop Powered | - | -
16 | A | 01PI0002 | 01-PT-0002 | P-102 Discharge Pressure | P-102 | 24E11-P1-PI-1004 | A | AI | 4~20mA | Loop Powered | - | -
17 | A | 01PI0003 | 01-PT-0003 | P-103 Discharge Pressure | P-103 | 24E11-P1-PI-1004 | A | AI | 4~20mA | Loop Powered | - | -
18 | A | 01PI0004 | 01-PT-0004 | P-104 Discharge Pressure | P-104 | 24E11-P1-PI-1004 | A | AI | 4~20mA | Loop Powered | - | -
19 | A | 01PI0005 | 01-PT-0005 | P-105 Discharge Pressure | P-105 | 24E11-P1-PI-1004 | A | AI | 4~20mA | Loop Powered | - | -
20 | A | 01PI0006 | 01-PT-0006 | P-106 Discharge Pressure | P-106 | 24E11-P1-PI-1004 | A | AI | 4~20mA | Loop Powered | - | -
21 | A | 01PI0007 | 01-PT-0007 | P-107 Discharge Pressure | P-107 | 24E11-P1-PI-1004 | A | AI | 4~20mA | Loop Powered | - | -
22 | A | 01HS0001A | 01-HS-0001A | Remote/Off/Local Switch | P-101 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | Remote | Local/Off
23 | 0 | 01HS0001BA | 01-HS-0001B | Start Switch | P-101 | 24E11-P1-PI-1004 | A | DO | Dry Contact | - | - | Start
24 | 0 | 01HS0001BB | 01-HS-0001B | Stop Switch | P-101 | 24E11-P1-PI-1004 | A | DO | Dry Contact | - | - | Stop
25 | A | 01HS0001C | 01-HS-0001C | Running/Trip | P-101 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | Trip | Running
26 | A | 01SC0001 | 01-SC-0001 | VSD Speed Control | P-101 | 24E11-P1-PI-1004 | A | AO | 4~20mA |  | - | -
27 | A | 01HS0002A | 01-HS-0002A | Remote/Off/Local Switch | P-102 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | Remote | Local/Off
28 | 0 | 01HS0002BA | 01-HS-0002B | Start Switch | P-102 | 24E11-P1-PI-1004 | A | DO | Dry Contact | - | - | Start
29 | 0 | 01HS0002BB | 01-HS-0002B | Stop Switch | P-102 | 24E11-P1-PI-1004 | A | DO | Dry Contact | - | - | Stop
30 | A | 01HS0002C | 01-HS-0002C | Running/Trip | P-102 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | Trip | Running
31 | A | 01SC0002 | 01-SC-0002 | VSD Speed Control | P-102 | 24E11-P1-PI-1004 | A | AO | 4~20mA |  | - | -
32 | A | 01HS0003A | 01-HS-0003A | Remote/Off/Local Switch | P-103 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | Remote | Local/Off
33 | 0 | 01HS0003BA | 01-HS-0003B | Start Switch | P-103 | 24E11-P1-PI-1004 | A | DO | Dry Contact | - | - | Start
34 | 0 | 01HS0003BB | 01-HS-0003B | Stop Switch | P-103 | 24E11-P1-PI-1004 | A | DO | Dry Contact | - | - | Stop
35 | A | 01HS0003C | 01-HS-0003C | Running/Trip | P-103 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | Trip | Running
36 | A | 01SC0003 | 01-SC-0003 | VSD Speed Control | P-103 | 24E11-P1-PI-1004 | A | AO | 4~20mA |  | - | -
37 | A | 01HS0004A | 01-HS-0004A | Remote/Off/Local Switch | P-104 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | Remote | Local/Off
38 | 0 | 01HS0004BA | 01-HS-0004B | Start Switch | P-104 | 24E11-P1-PI-1004 | A | DO | Dry Contact | - | - | Start
39 | 0 | 01HS0004BB | 01-HS-0004B | Stop Switch | P-104 | 24E11-P1-PI-1004 | A | DO | Dry Contact | - | - | Stop
40 | A | 01HS0004C | 01-HS-0004C | Running/Trip | P-104 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | Trip | Running
41 | A | 01SC0004 | 01-SC-0004 | VSD Speed Control | P-104 | 24E11-P1-PI-1004 | A | AO | 4~20mA |  | - | -
42 | A | 01HS0005A | 01-HS-0005A | Remote/Off/Local Switch | P-105 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | Remote | Local/Off
43 | 0 | 01HS0005BA | 01-HS-0005B | Start Switch | P-105 | 24E11-P1-PI-1004 | A | DO | Dry Contact | - | - | Start
44 | 0 | 01HS0005BB | 01-HS-0005B | Stop Switch | P-105 | 24E11-P1-PI-1004 | A | DO | Dry Contact | - | - | Stop
45 | A | 01HS0005C | 01-HS-0005C | Running/Trip | P-105 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | Trip | Running
46 | A | 01SC0005 | 01-SC-0005 | VSD Speed Control | P-105 | 24E11-P1-PI-1004 | A | AO | 4~20mA |  | - | -
47 | A | 01HS0006A | 01-HS-0006A | Remote/Off/Local Switch | P-106 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | Remote | Local/Off
48 | 0 | 01HS0006BA | 01-HS-0006B | Start Switch | P-106 | 24E11-P1-PI-1004 | A | DO | Dry Contact | - | - | Start
49 | 0 | 01HS0006BB | 01-HS-0006B | Stop Switch | P-106 | 24E11-P1-PI-1004 | A | DO | Dry Contact | - | - | Stop
50 | A | 01HS0006C | 01-HS-0006C | Running/Trip | P-106 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | Trip | Running
51 | A | 01SC0006 | 01-SC-0006 | VSD Speed Control | P-106 | 24E11-P1-PI-1004 | A | AO | 4~20mA |  | - | -
52 | A | 01HS0007A | 01-HS-0007A | Remote/Off/Local Switch | P-107 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | Remote | Local/Off
53 | 0 | 01HS0007BA | 01-HS-0007B | Start Switch | P-107 | 24E11-P1-PI-1004 | A | DO | Dry Contact | - | - | Start
54 | 0 | 01HS0007BB | 01-HS-0007B | Stop Switch | P-107 | 24E11-P1-PI-1004 | A | DO | Dry Contact | - | - | Stop
55 | A | 01HS0007C | 01-HS-0007C | Running/Trip | P-107 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | Trip | Running
56 | 0 | 04HS0001A | 04-HS-0001A | Remote/Off/Local Switch | P-401 | 24E11-P1-PI-1005 | A | DI | Dry Contact | - | Remote | Local/Off
57 | 0 | 04HS0001BA | 04-HS-0001B | Start Switch | P-401 | 24E11-P1-PI-1005 | A | DO | Dry Contact | - | - | Start
58 | 0 | 04HS0001BB | 04-HS-0001B | Stop Switch | P-401 | 24E11-P1-PI-1005 | A | DO | Dry Contact | - | - | Stop
59 | 0 | 04HS0001C | 04-HS-0001C | Running/Trip | P-401 | 24E11-P1-PI-1005 | A | DI | Dry Contact | - | Trip | Running

## JETTY
S/N | Revision No. | DCS Tag Number | Instrument Tag No. | Signal Description | Equipment | P & ID Dwg No. | P&ID Revision No. | IO Type | Signal Type | Power | Zero Stauts | One Stauts | Alarm Setting |  |  |  | Range |  | Unit | RIO Panel No. | Slot Number | Channel Number | Remarks
[13 empty] | LL | L | H | HH | 0% | 100% | [5 empty] | used | spare
INSTRUMENT I/O FOR JETTY AREA
1 | A | 03PI0001 | 03-PT-0001 | PLR-301 Discharge Line Pressure | PL-0301-8''-150A1 | 24E11-P1-PI-1001 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 16 | Barg |  |  |  | HOLD
2 | A | 03ZLL0001 | 03-ZSL-0001 | 03-MOV-0001 Fully Closed | 03-MOV-0001 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Closed
3 | A | 03ZLH0001 | 03-ZSH-0001 | 03-MOV-0001 Fully Open | 03-MOV-0001 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Open
4 | A | 03XS0001 | 03-HS-0001 | Local/Remote/Off Switch | 03-MOV-0001 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | Remote | Local/Off
5 | 0 | 03XA0001 | 03-XA-0001 | Fault | 03-MOV-0001 | 24E11-P1-PI-1001 | A | DI | Dry Contact | - | - | Alarm
6 | A | 03HSC0001 | 03-MOV-0001 | 03-MOV-0001 Close Command | 03-MOV-0001 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Open
7 | A | 03HSO0001 | 03-MOV-0001 | 03-MOV-0001 Open Command | 03-MOV-0001 | 24E11-P1-PI-1001 | A | DO | Dry Contact | - | - | Close

## TLB
S/N | Revision No. | DCS Tag Number | Instrument Tag No. | Signal Description | Equipment | P & ID Dwg No. | P&ID Revision No. | IO Type | Signal Type | Power | Zero Stauts | One Stauts | Alarm Setting |  |  |  | Range |  | Unit | RIO Panel No. | Slot Number | Channel Number | Remarks
[13 empty] | LL | L | H | HH | 0% | 100% | [5 empty] | used | spare
INSTRUMENT I/O FOR TRUCK LOADING AREA
1 | A | 04FI0101 | 04-FT-0101 | PLR-402 To Tuck Loading Bay 1 Line Flow | PL-0408-4"-150A1 | 24E11-P1-PI-1005 | A | AI | 4~20mA | Loop Powered | - | - | [10 empty] | HOLD
2 | A | 04FI0201 | 04-FT-0201 | PLR-402 To Tuck Loading Bay 2 Line Flow | PL-0409-4"-150A1 | 24E11-P1-PI-1005 | A | AI | 4~20mA | Loop Powered | - | - | [10 empty] | HOLD
3 | A | 04FI0301 | 04-FT-0301 | PLR-403 To Tuck Loading Bay 3 Line Flow | PL-0412-4"-150A1 | 24E11-P1-PI-1005 | A | AI | 4~20mA | Loop Powered | - | - | [10 empty] | HOLD
4 | A | 04FI0401 | 04-FT-0401 | PLR-403 To Tuck Loading Bay 4 Line Flow | PL-0413-4"-150A1 | 24E11-P1-PI-1005 | A | AI | 4~20mA | Loop Powered | - | - | [10 empty] | HOLD
5 | A | 04FI0501 | 04-FT-0501 | PLR-404 To Truck Loading Bay 5 Line Flow | PL-0416-4"-150A1 | 24E11-P1-PI-1006 | A | AI | 4~20mA | Loop Powered | - | - | [10 empty] | HOLD
6 | A | 04FI0601 | 04-FT-0601 | PLR-404 To Truck Loading Bay 6 Line Flow | PL-0417-4"-150A1 | 24E11-P1-PI-1006 | A | AI | 4~20mA | Loop Powered | - | - | [10 empty] | HOLD
7 | A | 04FI0701 | 04-FT-0701 | PLR-405 To Truck Loading Bay 7 Line Flow | PL-0420-4"-150A1 | 24E11-P1-PI-1006 | A | AI | 4~20mA | Loop Powered | - | - | [10 empty] | HOLD
8 | A | 04FI0801 | 04-FT-0801 | PLR-405 To Truck Loading Bay 8 Line Flow | PL-0421-4"-150A1 | 24E11-P1-PI-1006 | A | AI | 4~20mA | Loop Powered | - | - | [10 empty] | HOLD
9 | A | 04ZC0101 | 04-ZC-0101 | 04-FCV-0101 Opening Control | PL-0408-4"-150A1 | 24E11-P1-PI-1005 | A | AO | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | % |  |  |  | HOLD
10 | A | 04ZI0101 | 04-ZT-0101 | 04-FCV-0101 Opening Position Feedback | PL-0408-4"-150A1 | 24E11-P1-PI-1005 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | % |  |  |  | HOLD
11 | A | 04ZC0201 | 04-ZC-0201 | 04-FCV-0201 Opening Control | PL-0409-4"-150A1 | 24E11-P1-PI-1005 | A | AO | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | % |  |  |  | HOLD
12 | A | 04ZI0201 | 04-ZT-0201 | 04-FCV-0201 Opening Position Feedback | PL-0409-4"-150A1 | 24E11-P1-PI-1005 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | % |  |  |  | HOLD
13 | A | 04ZC0301 | 04-ZC-0301 | 04-FCV-0301 Opening Control | PL-0412-4"-150A1 | 24E11-P1-PI-1005 | A | AO | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | % |  |  |  | HOLD
14 | A | 04ZI0301 | 04-ZT-0301 | 04-FCV-0301 Opening Position Feedback | PL-0412-4"-150A1 | 24E11-P1-PI-1005 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | % |  |  |  | HOLD
15 | A | 04ZC0401 | 04-ZC-0401 | 04-FCV-0401 Opening Control | PL-0413-4"-150A1 | 24E11-P1-PI-1005 | A | AO | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | % |  |  |  | HOLD
16 | A | 04ZI0401 | 04-ZT-0401 | 04-FCV-0401 Opening Position Feedback | PL-0413-4"-150A1 | 24E11-P1-PI-1005 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | % |  |  |  | HOLD
17 | A | 04ZC0501 | 04-ZC-0501 | 04-FCV-0501 Opening Control | PL-0416-4"-150A1 | 24E11-P1-PI-1006 | A | AO | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | % |  |  |  | HOLD
18 | A | 04ZI0501 | 04-ZT-0501 | 04-FCV-0501 Opening Position Feedback | PL-0416-4"-150A1 | 24E11-P1-PI-1006 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | % |  |  |  | HOLD
19 | A | 04ZC0601 | 04-ZC-0601 | 04-FCV-0601 Opening Control | PL-0417-4"-150A1 | 24E11-P1-PI-1006 | A | AO | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | % |  |  |  | HOLD
20 | A | 04ZI0601 | 04-ZT-0601 | 04-FCV-0601 Opening Position Feedback | PL-0417-4"-150A1 | 24E11-P1-PI-1006 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | % |  |  |  | HOLD
21 | A | 04ZC0701 | 04-ZC-0701 | 04-FCV-0701 Opening Control | PL-0420-4"-150A1 | 24E11-P1-PI-1006 | A | AO | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | % |  |  |  | HOLD
22 | A | 04ZI0701 | 04-ZT-0701 | 04-FCV-0701 Opening Position Feedback | PL-0420-4"-150A1 | 24E11-P1-PI-1006 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | % |  |  |  | HOLD
23 | A | 04ZC0801 | 04-ZC-0801 | 04-FCV-0801 Opening Control | PL-0421-4"-150A1 | 24E11-P1-PI-1006 | A | AO | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | % |  |  |  | HOLD
24 | A | 04ZI0801 | 04-ZT-0801 | 04-FCV-0801 Opening Position Feedback | PL-0421-4"-150A1 | 24E11-P1-PI-1006 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | % |  |  |  | HOLD
25 | 0 | 04TI0101 | 04-TT-0101 | PLR-402 To Truck Loading Bay 1 Line Temperature | PL-0408-4"-150A1 | 24E11-P1-PI-1005 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | ℃ |  |  |  | HOLD
26 | 0 | 04TI0201 | 04-TT-0201 | PLR-402 To Truck Loading Bay 2 Line Temperature | PL-0409-4"-150A1 | 24E11-P1-PI-1005 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | ℃ |  |  |  | HOLD
27 | 0 | 04TI0301 | 04-TT-0301 | PLR-403 To Truck Loading Bay 3 Line Temperature | PL-0412-4"-150A1 | 24E11-P1-PI-1005 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | ℃ |  |  |  | HOLD
28 | 0 | 04TI0401 | 04-TT-0401 | PLR-403 To Truck Loading Bay 4 Line Temperature | PL-0413-4"-150A1 | 24E11-P1-PI-1005 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | ℃ |  |  |  | HOLD
29 | 0 | 04TI0501 | 04-TT-0501 | PLR-404 To Truck Loading Bay 5 Line Temperature | PL-0416-4"-150A1 | 24E11-P1-PI-1006 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | ℃ |  |  |  | HOLD
30 | 0 | 04TI0601 | 04-TT-0601 | PLR-404 To Truck Loading Bay 6 Line Temperature | PL-0417-4"-150A1 | 24E11-P1-PI-1006 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | ℃ |  |  |  | HOLD
31 | 0 | 04TI0701 | 04-TT-0701 | PLR-405 To Truck Loading Bay 7 Line Temperature | PL-0420-4"-150A1 | 24E11-P1-PI-1006 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | ℃ |  |  |  | HOLD
32 | 0 | 04TI0801 | 04-TT-0801 | PLR-405 To Truck Loading Bay 8 Line Temperature | PL-0421-4"-150A1 | 24E11-P1-PI-1006 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | ℃ |  |  |  | HOLD
33 | A | 04PI0101 | 04-PT-0101 | PLR-402 To Truck Loading Bay 1 Line Pressure | PL-0408-4"-150A1 | 24E11-P1-PI-1005 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 10 | Barg |  |  |  | HOLD
34 | A | 04PI0201 | 04-PT-0201 | PLR-402 To Truck Loading Bay 2 Line Pressure | PL-0409-4"-150A1 | 24E11-P1-PI-1005 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 10 | Barg |  |  |  | HOLD
35 | A | 04PI0301 | 04-PT-0301 | PLR-403 To Truck Loading Bay 3 Line Pressure | PL-0412-4"-150A1 | 24E11-P1-PI-1005 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 10 | Barg |  |  |  | HOLD
36 | A | 04PI0401 | 04-PT-0401 | PLR-403 To Truck Loading Bay 4 Line Pressure | PL-0413-4"-150A1 | 24E11-P1-PI-1005 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 10 | Barg |  |  |  | HOLD
37 | A | 04PI0501 | 04-PT-0501 | PLR-404 To Truck Loading Bay 5 Line Pressure | PL-0416-4"-150A1 | 24E11-P1-PI-1006 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 10 | Barg |  |  |  | HOLD
38 | A | 04PI0601 | 04-PT-0601 | PLR-404 To Truck Loading Bay 6 Line Pressure | PL-0417-4"-150A1 | 24E11-P1-PI-1006 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 10 | Barg |  |  |  | HOLD
39 | A | 04PI0701 | 04-PT-0701 | PLR-405 To Truck Loading Bay 7 Line Pressure | PL-0420-4"-150A1 | 24E11-P1-PI-1006 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 10 | Barg |  |  |  | HOLD
40 | A | 04PI0801 | 04-PT-0801 | PLR-405 To Truck Loading Bay 8 Line Pressure | PL-0421-4"-150A1 | 24E11-P1-PI-1006 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 10 | Barg |  |  |  | HOLD
41 | A | 04ZLL0101 | 04-ZSL-0101 | 04-MOV-0101 Fully Closed | 04-MOV-0101 | 24E11-P1-PI-1005 | A | DI | Dry Contact | - | - | Closed
42 | A | 04ZLH0101 | 04-ZSH-0101 | 04-MOV-0101 Fully Open | 04-MOV-0101 | 24E11-P1-PI-1005 | A | DI | Dry Contact | - | - | Open
43 | A | 04XS0101 | 04-HS-0101 | Local/Remote/Off Switch | 04-MOV-0101 | 24E11-P1-PI-1005 | A | DI | Dry Contact | - | Remote | Local/Off
44 | 0 | 04XA0101 | 04-XA-0101 | Fault | 04-MOV-0101 | 24E11-P1-PI-1005 | A | DI | Dry Contact | - | - | Alarm
45 | A | 04HSC0101 | 04-MOV-0101 | 04-MOV-0101 Close Command | 04-MOV-0101 | 24E11-P1-PI-1005 | A | DO | Dry Contact | - | - | Open
46 | A | 04HSO0101 | 04-MOV-0101 | 04-MOV-0101 Open Command | 04-MOV-0101 | 24E11-P1-PI-1005 | A | DO | Dry Contact | - | - | Close
47 | A | 04ZLL0201 | 04-ZSL-0201 | 04-MOV-0201 Fully Closed | 04-MOV-0201 | 24E11-P1-PI-1005 | A | DI | Dry Contact | - | - | Closed
48 | A | 04ZLH0201 | 04-ZSH-0201 | 04-MOV-0201 Fully Open | 04-MOV-0201 | 24E11-P1-PI-1005 | A | DI | Dry Contact | - | - | Open
49 | A | 04XS0201 | 04-HS-0201 | Local/Remote/Off Switch | 04-MOV-0201 | 24E11-P1-PI-1005 | A | DI | Dry Contact | - | Remote | Local/Off
50 | 0 | 04XA0201 | 04-XA-0201 | Fault | 04-MOV-0201 | 24E11-P1-PI-1005 | A | DI | Dry Contact | - | - | Alarm
51 | A | 04HSC0201 | 04-MOV-0201 | 04-MOV-0201 Close Command | 04-MOV-0201 | 24E11-P1-PI-1005 | A | DO | Dry Contact | - | - | Open
52 | A | 04HSO0201 | 04-MOV-0201 | 04-MOV-0201 Open Command | 04-MOV-0201 | 24E11-P1-PI-1005 | A | DO | Dry Contact | - | - | Close
53 | A | 04ZLL0301 | 04-ZSL-0301 | 04-MOV-0301 Fully Closed | 04-MOV-0301 | 24E11-P1-PI-1005 | A | DI | Dry Contact | - | - | Closed
54 | A | 04ZLH0301 | 04-ZSH-0301 | 04-MOV-0301 Fully Open | 04-MOV-0301 | 24E11-P1-PI-1005 | A | DI | Dry Contact | - | - | Open
55 | A | 04XS0301 | 04-HS-0301 | Local/Remote/Off Switch | 04-MOV-0301 | 24E11-P1-PI-1005 | A | DI | Dry Contact | - | Remote | Local/Off
56 | 0 | 04XA0301 | 04-XA-0301 | Fault | 04-MOV-0301 | 24E11-P1-PI-1005 | A | DI | Dry Contact | - | - | Alarm
57 | A | 04HSC0301 | 04-MOV-0301 | 04-MOV-0301 Close Command | 04-MOV-0301 | 24E11-P1-PI-1005 | A | DO | Dry Contact | - | - | Open
58 | A | 04HSO0301 | 04-MOV-0301 | 04-MOV-0301 Open Command | 04-MOV-0301 | 24E11-P1-PI-1005 | A | DO | Dry Contact | - | - | Close
59 | A | 04ZLL0401 | 04-ZSL-0401 | 04-MOV-0401 Fully Closed | 04-MOV-0401 | 24E11-P1-PI-1005 | A | DI | Dry Contact | - | - | Closed
60 | A | 04ZLH0401 | 04-ZSH-0401 | 04-MOV-0401 Fully Open | 04-MOV-0401 | 24E11-P1-PI-1005 | A | DI | Dry Contact | - | - | Open
61 | A | 04XS0401 | 04-HS-0401 | Local/Remote/Off Switch | 04-MOV-0401 | 24E11-P1-PI-1005 | A | DI | Dry Contact | - | Remote | Local/Off
62 | 0 | 04XA0401 | 04-XA-0401 | Fault | 04-MOV-0401 | 24E11-P1-PI-1005 | A | DI | Dry Contact | - | - | Alarm
63 | A | 04HSC0401 | 04-MOV-0401 | 04-MOV-0401 Close Command | 04-MOV-0401 | 24E11-P1-PI-1005 | A | DO | Dry Contact | - | - | Open
64 | A | 04HSO0401 | 04-MOV-0401 | 04-MOV-0401 Open Command | 04-MOV-0401 | 24E11-P1-PI-1005 | A | DO | Dry Contact | - | - | Close
65 | A | 04ZLL0501 | 04-ZSL-0501 | 04-MOV-0501 Fully Closed | 04-MOV-0501 | 24E11-P1-PI-1006 | A | DI | Dry Contact | - | - | Closed
66 | A | 04ZLH0501 | 04-ZSH-0501 | 04-MOV-0501 Fully Open | 04-MOV-0501 | 24E11-P1-PI-1006 | A | DI | Dry Contact | - | - | Open
67 | A | 04XS0501 | 04-HS-0501 | Local/Remote/Off Switch | 04-MOV-0501 | 24E11-P1-PI-1006 | A | DI | Dry Contact | - | Remote | Local/Off
68 | 0 | 04XA0501 | 04-XA-0501 | Fault | 04-MOV-0501 | 24E11-P1-PI-1006 | A | DI | Dry Contact | - | - | Alarm
69 | A | 04HSC0501 | 04-MOV-0501 | 04-MOV-0501 Close Command | 04-MOV-0501 | 24E11-P1-PI-1006 | A | DO | Dry Contact | - | - | Open
70 | A | 04HSO0501 | 04-MOV-0501 | 04-MOV-0501 Open Command | 04-MOV-0501 | 24E11-P1-PI-1006 | A | DO | Dry Contact | - | - | Close
71 | A | 04ZLL0601 | 04-ZSL-0601 | 04-MOV-0601 Fully Closed | 04-MOV-0601 | 24E11-P1-PI-1006 | A | DI | Dry Contact | - | - | Closed
72 | A | 04ZLH0601 | 04-ZSH-0601 | 04-MOV-0601 Fully Open | 04-MOV-0601 | 24E11-P1-PI-1006 | A | DI | Dry Contact | - | - | Open
73 | A | 04XS0601 | 04-HS-0601 | Local/Remote/Off Switch | 04-MOV-0601 | 24E11-P1-PI-1006 | A | DI | Dry Contact | - | Remote | Local/Off
74 | 0 | 04XA0601 | 04-XA-0601 | Fault | 04-MOV-0601 | 24E11-P1-PI-1006 | A | DI | Dry Contact | - | - | Alarm
75 | A | 04HSC0601 | 04-MOV-0601 | 04-MOV-0601 Close Command | 04-MOV-0601 | 24E11-P1-PI-1006 | A | DO | Dry Contact | - | - | Open
76 | A | 04HSO0601 | 04-MOV-0601 | 04-MOV-0601 Open Command | 04-MOV-0601 | 24E11-P1-PI-1006 | A | DO | Dry Contact | - | - | Close
77 | A | 04ZLL0701 | 04-ZSL-0701 | 04-MOV-0701 Fully Closed | 04-MOV-0701 | 24E11-P1-PI-1006 | A | DI | Dry Contact | - | - | Closed
78 | A | 04ZLH0701 | 04-ZSH-0701 | 04-MOV-0701 Fully Open | 04-MOV-0701 | 24E11-P1-PI-1006 | A | DI | Dry Contact | - | - | Open
79 | A | 04XS0701 | 04-HS-0701 | Local/Remote/Off Switch | 04-MOV-0701 | 24E11-P1-PI-1006 | A | DI | Dry Contact | - | Remote | Local/Off
80 | 0 | 04XA0701 | 04-XA-0701 | Fault | 04-MOV-0701 | 24E11-P1-PI-1006 | A | DI | Dry Contact | - | - | Alarm
81 | A | 04HSC0701 | 04-MOV-0701 | 04-MOV-0701 Close Command | 04-MOV-0701 | 24E11-P1-PI-1006 | A | DO | Dry Contact | - | - | Open
82 | A | 04HSO0701 | 04-MOV-0701 | 04-MOV-0701 Open Command | 04-MOV-0701 | 24E11-P1-PI-1006 | A | DO | Dry Contact | - | - | Close
83 | A | 04ZLL0801 | 04-ZSL-0801 | 04-MOV-0801 Fully Closed | 04-MOV-0801 | 24E11-P1-PI-1006 | A | DI | Dry Contact | - | - | Closed
84 | A | 04ZLH0801 | 04-ZSH-0801 | 04-MOV-0801 Fully Open | 04-MOV-0801 | 24E11-P1-PI-1006 | A | DI | Dry Contact | - | - | Open
85 | A | 04XS0801 | 04-HS-0801 | Local/Remote/Off Switch | 04-MOV-0801 | 24E11-P1-PI-1006 | A | DI | Dry Contact | - | Remote | Local/Off
86 | 0 | 04XA0801 | 04-XA-0801 | Fault | 04-MOV-0801 | 24E11-P1-PI-1006 | A | DI | Dry Contact | - | - | Alarm
87 | A | 04HSC0801 | 04-MOV-0801 | 04-MOV-0801 Close Command | 04-MOV-0801 | 24E11-P1-PI-1006 | A | DO | Dry Contact | - | - | Open
88 | A | 04HSO0801 | 04-MOV-0801 | 04-MOV-0801 Open Command | 04-MOV-0801 | 24E11-P1-PI-1006 | A | DO | Dry Contact | - | - | Close
89 | A | 04LAHH0101 | 04-LS-0101 | TLA-401 Overfilling Protection | TLA-401 | 24E11-P1-PI-1005 | A | DI | Dry Contact |  |  | H Level | [10 empty] | HOLD
90 | A | 04LAHH0201 | 04-LS-0201 | TLA-402 Overfilling Protection | TLA-402 | 24E11-P1-PI-1005 | A | DI | Dry Contact |  |  | H Level | [10 empty] | HOLD
91 | A | 04LAHH0301 | 04-LS-0301 | TLA-403 Overfilling Protection | TLA-403 | 24E11-P1-PI-1005 | A | DI | Dry Contact |  |  | H Level | [10 empty] | HOLD
92 | A | 04LAHH0401 | 04-LS-0401 | TLA-404 Overfilling Protection | TLA-404 | 24E11-P1-PI-1005 | A | DI | Dry Contact |  |  | H Level | [10 empty] | HOLD
93 | A | 04LAHH0501 | 04-LS-0501 | TLA-405 Overfilling Protection | TLA-405 | 24E11-P1-PI-1006 | A | DI | Dry Contact |  |  | H Level | [10 empty] | HOLD
94 | A | 04LAHH0601 | 04-LS-0601 | TLA-406 Overfilling Protection | TLA-406 | 24E11-P1-PI-1006 | A | DI | Dry Contact |  |  | H Level | [10 empty] | HOLD
95 | A | 04LAHH0701 | 04-LS-0701 | TLA-407 Overfilling Protection | TLA-407 | 24E11-P1-PI-1006 | A | DI | Dry Contact |  |  | H Level | [10 empty] | HOLD
96 | A | 04LAHH0801 | 04-LS-0801 | TLA-408 Overfilling Protection | TLA-408 | 24E11-P1-PI-1006 | A | DI | Dry Contact |  |  | H Level | [10 empty] | HOLD
97 | A | 04ED0001 | 04-ED-0001 | TLB 1 Grouding Unit | TLB 1 | 24E11-P1-PI-1005 | A | DI | Dry Contact |  | Normal | Grounding Fault | [10 empty] | HOLD
98 | A | 04ED0002 | 04-ED-0002 | TLB 2 Grouding Unit | TLB 2 | 24E11-P1-PI-1005 | A | DI | Dry Contact |  | Normal | Grounding Fault | [10 empty] | HOLD
99 | A | 04ED0003 | 04-ED-0003 | TLB 3 Grouding Unit | TLB 3 | 24E11-P1-PI-1005 | A | DI | Dry Contact |  | Normal | Grounding Fault | [10 empty] | HOLD
100 | A | 04ED0004 | 04-ED-0004 | TLB 4 Grouding Unit | TLB 4 | 24E11-P1-PI-1005 | A | DI | Dry Contact |  | Normal | Grounding Fault | [10 empty] | HOLD
101 | A | 04ED0005 | 04-ED-0005 | TLB 5 Grouding Unit | TLB 5 | 24E11-P1-PI-1006 | A | DI | Dry Contact |  | Normal | Grounding Fault | [10 empty] | HOLD
102 | A | 04ED0006 | 04-ED-0006 | TLB 6 Grouding Unit | TLB 6 | 24E11-P1-PI-1006 | A | DI | Dry Contact |  | Normal | Grounding Fault | [10 empty] | HOLD
103 | A | 04ED0007 | 04-ED-0007 | TLB 7 Grouding Unit | TLB 7 | 24E11-P1-PI-1006 | A | DI | Dry Contact |  | Normal | Grounding Fault | [10 empty] | HOLD
104 | A | 04ED0008 | 04-ED-0008 | TLB 8 Grouding Unit | TLB 8 | 24E11-P1-PI-1006 | A | DI | Dry Contact |  | Normal | Grounding Fault | [10 empty] | HOLD
105 | A | 04PI0001 | 04-PT-0001 | P-401 Discharge Pressure | P-401 | 24E11-P1-PI-1005 | A | AI | 4~20mA | Loop Powered | - | -

## FIRE F (hidden)
S/N | Revision No. | DCS Tag Number | Instrument Tag No. | Signal Description | Equipment | P & ID Dwg No. | P&ID Revision No. | IO Type | Signal Type | Power | Zero Stauts | One Stauts | Alarm Setting |  |  |  | Range |  | Unit | RIO Panel No. | Slot Number | Channel Number | Remarks
[13 empty] | LL | L | H | HH | 0% | 100% | [5 empty] | used | spare
INSTRUMENT I/O FOR FIRE FIGHTING SYSTEM
1 | A | 07FI0001 | 07-FT-0001 | Municipal Water To T-701 Line Flow | FW-0001-4"-150B | 24E11-P1-PI-1010 | A | AI | 4~20mA | Loop Powered | - | -
2 | A | 07LI0101 | 07-LT-0101 | T-701 Level | T-701 | 24E11-P1-PI-1010 | A | AI | 4~20mA | Loop Powered | - | -
3 | A | 07PI0001 | 07-PT-0001 | Firefighting Water Suppy Bus Pressure | FW-0014-6"-150B | 24E11-P1-PI-1010 | A | AI | 4~20mA | Loop Powered | - | -
4 | A | 07LSL0101 | 07-LSL-0101 | P-701 Diesel Oil Tank Low Level Protection | P-701 | 24E11-P1-PI-1010 | A | DI | Dry Contact | - | - | L Level
5 | A | 07LSL0201 | 07-LSL-0201 | P-702 Diesel Oil Tank Low Level Protection | P-702 | 24E11-P1-PI-1010 | A | DI | Dry Contact | - | - | L Level

## HOT WATER
S/N | Revision No. | DCS Tag Number | Instrument Tag No. | Signal Description | Equipment | P & ID Dwg No. | P&ID Revision No. | IO Type | Signal Type | Power | Zero Stauts | One Stauts | Alarm Setting |  |  |  | Range |  | Unit | RIO Panel No. | Slot Number | Channel Number | Remarks
[13 empty] | LL | L | H | HH | 0% | 100% | [5 empty] | used | spare
INSTRUMENT I/O FOR HOT WATER SYSTEM
1 | A | 08LI0101 | 08-LT-0101 | T-801 Level | T-801 | 24E11-P1-PI-1009 | A | AI | 4~20mA | Loop Powered | - | -
2 | A | 08TI0001 | 08-TT-0001 | T-801 Discharge Temperature | B-801 | 24E11-P1-PI-1009 | A | AI | 4~20mA | Loop Powered | - | -
3 | A | 08TI0002 | 08-TT-0002 | B-801 Discharge Temperature | B-801 | 24E11-P1-PI-1009 | A | AI | 4~20mA | Loop Powered | - | -
4 | A | 08TI0003 | 08-TT-0003 | B-801 Suction Temperature | B-801 | 24E11-P1-PI-1009 | A | AI | 4~20mA | Loop Powered | - | -
5 | A |  | 08-LSL-0001 | V-801 Low Level Protection | V-801 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | L Level
6 | A |  | 08-LSH-0001 | V-801 High Level Protection | V-801 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | H Level
7 | A |  | 08-HS-0001A/B | Running Status | P-801 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | Running
8 | A |  | 08-HS-0001A/B | Duty Status | P-801 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | Duty
9 | A |  | 08-HS-0001A/B | Standby Status | P-801 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | Standby
10 | A |  | 08-HS-0001A/B | Trip Status | P-801 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | Trip
11 | A |  | 08-HS-0002A/B | Running Status | P-802 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | Running
12 | A |  | 08-HS-0002A/B | Duty Status | P-802 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | Duty
13 | A |  | 08-HS-0002A/B | Standby Status | P-802 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | Standby
14 | A |  | 08-HS-0002A/B | Trip Status | P-802 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | Trip
15 | A |  | 08-HS-0003A/B | Running Status | P-803 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | Running
16 | A |  | 08-HS-0003A/B | Duty Status | P-803 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | Duty
17 | A |  | 08-HS-0003A/B | Standby Status | P-803 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | Standby
18 | A |  | 08-HS-0003A/B | Trip Status | P-803 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | Trip
19 | A |  | 08-HS-0004A/B | Running Status | P-804 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | Running
20 | A |  | 08-HS-0004A/B | Duty Status | P-804 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | Duty
21 | A |  | 08-HS-0004A/B | Standby Status | P-804 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | Standby
22 | A |  | 08-HS-0004A/B | Trip Status | P-804 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | Trip
23 | A |  | 08-HS-B001 | Running Status | B-801 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | Running
24 | A |  | 08-HS-B001 | Duty Status | B-801 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | Duty
25 | A |  | 08-HS-B001 | Standby Status | B-801 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | Standby
26 | A |  | 08-HS-B001 | Trip Status | B-801 | 24E11-P1-PI-1009 | A | DI | Dry Contact | - | - | Trip

## POTABLE WATER
S/N | Revision No. | DCS Tag Number | Instrument Tag No. | Signal Description | Equipment | P & ID Dwg No. | P&ID Revision No. | IO Type | Signal Type | Power | Zero Stauts | One Stauts | Alarm Setting |  |  |  | Range |  | Unit | RIO Panel No. | Slot Number | Channel Number | Remarks
[13 empty] | LL | L | H | HH | 0% | 100% | [5 empty] | used | spare
INSTRUMENT I/O FOR POTABLE WATER SYSTEM
1 | A | 05FI0001 | 05-FT-0001 | Municipal Water To T-501 Line Flow | T-501 | 24E11-P1-PI-1007 | A | AI | 4~20mA | Loop Powered | - | -
2 | A | 05LI0101 | 05-LT-0101 | T-501 Level | T-501 | 24E11-P1-PI-1007 | A | AI | 4~20mA | Loop Powered | - | -
3 | A | 05PI0001 | 05-PT-0001 | Potable Water Suppy Bus Pressure | PW-0009-3"-150A3 | 24E11-P1-PI-1007 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 6 | Barg
4 | A | 05PA0001 | 05-PS-0001 | Potable Water Suppy Bus H/L Pressure Protection | PW-0009-3"-150A3 | 24E11-P1-PI-1007 | A | DI | Dry Contact | - | - | H/L |  | 2.5 | 5.5 |  |  |  | Barg
5 | A |  | 05-HS-0001A/B | Running Status | P-501 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | - | Running
6 | A |  | 05-HS-0001A/B | Duty Status | P-501 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | - | Duty
7 | A |  | 05-HS-0001A/B | Standby Status | P-501 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | - | Standby
8 | A |  | 05-HS-0001A/B | Trip Status | P-501 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | - | Trip
9 | A |  | 05-HS-0002A/B | Running Status | P-502 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | - | Running
10 | A |  | 05-HS-0002A/B | Duty Status | P-502 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | - | Duty
11 | A |  | 05-HS-0002A/B | Standby Status | P-502 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | - | Standby
12 | A |  | 05-HS-0002A/B | Trip Status | P-502 | 24E11-P1-PI-1004 | A | DI | Dry Contact | - | - | Trip

## PLANT AIR
S/N | Revision No. | DCS Tag Number | Instrument Tag No. | Signal Description | Equipment | P & ID Dwg No. | P&ID Revision No. | IO Type | Signal Type | Power | Zero Stauts | One Stauts | Alarm Setting |  |  |  | Range |  | Unit | RIO Panel No. | Slot Number | Channel Number | Remarks
[13 empty] | LL | L | H | HH | 0% | 100% | [5 empty] | used | spare
INSTRUMENT I/O FOR PLANT AIR SYETEM
1 | A | 06PI0001 | 06-PT-0001 | V-601 Pressure | V-601 | 24E11-P1-PI-1008 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 10 | Barg
2 | A | 06PI0002 | 06-PT-0002 | V-602 Pressure | V-602 | 24E11-P1-PI-1008 | A | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 10 | Barg
3 | A | 06XA0001 | 06-XA-0001 | C-601 Fault | C-601 | 24E11-P1-PI-1008 | A | DI | Dry Contact | - | - | Fault
4 | A | 06ZI0001 | 06-ZI-0001 | C-601 Running/Stop | C-601 | 24E11-P1-PI-1008 | A | DI | Dry Contact | - | Stop | Running
5 | A | 06XI001 | 06-XI-0001 | C-601 Loading/unloading | C-601 | 24E11-P1-PI-1008 | A | DI | Dry Contact | - | Loading | Unloading
6 | A | 06XA0002 | 06-XA-0002 | C-602 Fault | C-602 | 24E11-P1-PI-1008 | A | DI | Dry Contact | - | - | Fault
7 | A | 06ZI0002 | 06-ZI-0002 | C-602 Running/Stop | C-602 | 24E11-P1-PI-1008 | A | DI | Dry Contact | - | Stop | Running
8 | A | 06XI002 | 06-XI-0002 | C-602 Loading/unloading | C-602 | 24E11-P1-PI-1008 | A | DI | Dry Contact | - | Loading | Unloading

## TEMPLATE (hidden)
S/N | Revision No. | DCS Tag Number | Instrument Tag No. | Signal Description | Equipment | P & ID Dwg No. | P&ID Revision No. | IO Type | Signal Type | Zero Stauts | One Stauts | Alarm Setting |  |  |  | Range |  | Unit | RIO Panel No. | Slot Number | Channel Number | Remarks
[12 empty] | LL | L | H | HH | 0% | 100% | [5 empty] | used | spare
TRUCK LOADING BAY
1 | O1 | 41-LAH-0101 | 41-LSH-0101 | 41-TLA-001 Overfilling Protection | 41-TLA-001 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact |  | H Level
2 | O1 | 41-ZI-0101 | 41-WCV-0101 | 41-WCV-01 Opening Position Feedback | 41-TLA-001 | 22E20-C01-P1-PID-3001 | 2 | AI | 4~20mA | [6 empty] | 0 | 100 | %
3 | O1 | 41-ZC-0101 | 41-WCV-0101 | 41-WCV-01 Opening Control Signal | 41-TLA-001 | 22E20-C01-P1-PID-3001 | 2 | AO | 4~20mA | [6 empty] | 0 | 100 | %
4 | O1 | 41-ZLH-001 | 41-TLA-001 | 41-TLA-001 Truck Loading Arm Parked | 41-TLA-001 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact |  | Parked
5 | O1 | 41-ZLL-001 | 41-TLA-001 | 41-TLA-001 Truck Loading Arm Extended | 41-TLA-001 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact |  | Extended
6 | O1 | 41-LAH-0201 | 41-LSH-0201 | 41-TLA-002 Overfilling Protection | 41-TLA-002 | 22E20-C01-P1-PID-4002 | 2 | DI | Dry Contact |  | H Level
7 | O1 | 41-ZI-0201 | 41-WCV-0201 | 41-WCV-01 Opening Position Feedback | 41-TLA-002 | 22E20-C01-P1-PID-3002 | 2 | AI | 4~20mA | [6 empty] | 0 | 100 | %
8 | O1 | 41-ZC-0201 | 41-WCV-0201 | 41-WCV-01 Opening Control Signal | 41-TLA-002 | 22E20-C01-P1-PID-3002 | 2 | AO | 4~20mA | [6 empty] | 0 | 100 | %
9 | O1 | 41-ZLH-002 | 41-TLA-002 | 41-TLA-002 Truck Loading Arm Parked | 41-TLA-002 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact |  | Parked
10 | O1 | 41-ZLL-002 | 41-TLA-002 | 41-TLA-002 Truck Loading Arm Extended | 41-TLA-002 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact |  | Extended
11 | O1 | 41-ED-0001 | 41-ED-0001 | 41-TLB-001 Grouding Unit | 41-TLB-001 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact | Normal | Grounding Fault
12 | O1 | 41-AVA-0001 | 41-AVA-0001 | 41-TLB-001 Audible & Visual Alarm | 41-TLB-001 | 22E20-C01-P1-PID-4001 | 2 | DO | Dry Contact |  | Alarm
13 | O1 | 42-LAH-0101 | 42-LSH-0101 | 42-TLA-001 Overfilling Protection | 42-TLA-001 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact |  | H Level
14 | O1 | 42-ZI-0101 | 42-WCV-0101 | 42-WCV-01 Opening Position Feedback | 42-TLA-001 | 22E20-C01-P1-PID-3001 | 2 | AI | 4~20mA | [6 empty] | 0 | 100 | %
15 | O1 | 42-ZC-0101 | 42-WCV-0101 | 42-WCV-01 Opening Control Signal | 42-TLA-001 | 22E20-C01-P1-PID-3001 | 2 | AO | 4~20mA | [6 empty] | 0 | 100 | %
16 | O1 | 42-ZLH-001 | 42-TLA-001 | 42-TLA-001 Truck Loading Arm Parked | 42-TLA-001 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact |  | Parked
17 | O1 | 42-ZLL-001 | 42-TLA-001 | 42-TLA-001 Truck Loading Arm Extended | 42-TLA-001 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact |  | Extended
18 | O1 | 42-LAH-0201 | 42-LSH-0201 | 42-TLA-002 Overfilling Protection | 42-TLA-002 | 22E20-C01-P1-PID-4002 | 2 | DI | Dry Contact |  | H Level
19 | O1 | 42-ZI-0201 | 42-WCV-0201 | 42-WCV-01 Opening Position Feedback | 42-TLA-002 | 22E20-C01-P1-PID-3002 | 2 | AI | 4~20mA | [6 empty] | 0 | 100 | %
20 | O1 | 42-ZC-0201 | 42-WCV-0201 | 42-WCV-01 Opening Control Signal | 42-TLA-002 | 22E20-C01-P1-PID-3002 | 2 | AO | 4~20mA | [6 empty] | 0 | 100 | %
21 | O1 | 42-ZLH-002 | 42-TLA-002 | 42-TLA-002 Truck Loading Arm Parked | 42-TLA-002 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact |  | Parked
22 | O1 | 42-ZLL-002 | 42-TLA-002 | 42-TLA-002 Truck Loading Arm Extended | 42-TLA-002 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact |  | Extended
23 | O1 | 42-ED-0001 | 42-ED-0001 | 42-TLB-001 Grouding Unit | 42-TLB-001 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact | Normal | Grounding Fault
24 | O1 | 42-AVA-0001 | 42-AVA-0001 | 42-TLB-001 Audible & Visual Alarm | 42-TLB-001 | 22E20-C01-P1-PID-4001 | 2 | DO | Dry Contact |  | Alarm
25 | O1 | 43-LAH-0101 | 43-LSH-0101 | 43-TLA-001 Overfilling Protection | 43-TLA-001 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact |  | H Level
26 | O1 | 43-ZI-0101 | 43-WCV-0101 | 43-WCV-01 Opening Position Feedback | 43-TLA-001 | 22E20-C01-P1-PID-3001 | 2 | AI | 4~20mA | [6 empty] | 0 | 100 | %
27 | O1 | 43-ZC-0101 | 43-WCV-0101 | 43-WCV-01 Opening Control Signal | 43-TLA-001 | 22E20-C01-P1-PID-3001 | 2 | AO | 4~20mA | [6 empty] | 0 | 100 | %
28 | O1 | 43-ZLH-001 | 43-TLA-001 | 43-TLA-001 Truck Loading Arm Parked | 43-TLA-001 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact |  | Parked
29 | O1 | 43-ZLL-001 | 43-TLA-001 | 43-TLA-001 Truck Loading Arm Extended | 43-TLA-001 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact |  | Extended
30 | O1 | 43-LAH-0201 | 43-LSH-0201 | 43-TLA-002 Overfilling Protection | 43-TLA-002 | 22E20-C01-P1-PID-4002 | 2 | DI | Dry Contact |  | H Level
31 | O1 | 43-ZI-0201 | 43-WCV-0201 | 43-WCV-01 Opening Position Feedback | 43-TLA-002 | 22E20-C01-P1-PID-3002 | 2 | AI | 4~20mA | [6 empty] | 0 | 100 | %
32 | O1 | 43-ZC-0201 | 43-WCV-0201 | 43-WCV-01 Opening Control Signal | 43-TLA-002 | 22E20-C01-P1-PID-3002 | 2 | AO | 4~20mA | [6 empty] | 0 | 100 | %
33 | O1 | 43-ZLH-002 | 43-TLA-002 | 43-TLA-002 Truck Loading Arm Parked | 43-TLA-002 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact |  | Parked
34 | O1 | 43-ZLL-002 | 43-TLA-002 | 43-TLA-002 Truck Loading Arm Extended | 43-TLA-002 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact |  | Extended
35 | O1 | 43-ED-0001 | 43-ED-0001 | 43-TLB-001 Grouding Unit | 43-TLB-001 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact | Normal | Grounding Fault
36 | O1 | 43-AVA-0001 | 43-AVA-0001 | 43-TLB-001 Audible & Visual Alarm | 43-TLB-001 | 22E20-C01-P1-PID-4001 | 2 | DO | Dry Contact |  | Alarm
37 | O1 | 44-LAH-0101 | 44-LSH-0101 | 44-TLA-001 Overfilling Protection | 44-TLA-001 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact |  | H Level
38 | O1 | 44-ZI-0101 | 44-WCV-0101 | 44-WCV-01 Opening Position Feedback | 44-TLA-001 | 22E20-C01-P1-PID-3001 | 2 | AI | 4~20mA | [6 empty] | 0 | 100 | %
39 | O1 | 44-ZC-0101 | 44-WCV-0101 | 44-WCV-01 Opening Control Signal | 44-TLA-001 | 22E20-C01-P1-PID-3001 | 2 | AO | 4~20mA | [6 empty] | 0 | 100 | %
40 | O1 | 44-ZLH-001 | 44-TLA-001 | 44-TLA-001 Truck Loading Arm Parked | 44-TLA-001 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact |  | Parked
41 | O1 | 44-ZLL-001 | 44-TLA-001 | 44-TLA-001 Truck Loading Arm Extended | 44-TLA-001 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact |  | Extended
42 | O1 | 44-LAH-0201 | 44-LSH-0201 | 44-TLA-002 Overfilling Protection | 44-TLA-002 | 22E20-C01-P1-PID-4002 | 2 | DI | Dry Contact |  | H Level
43 | O1 | 44-ZI-0201 | 44-WCV-0201 | 44-WCV-01 Opening Position Feedback | 44-TLA-002 | 22E20-C01-P1-PID-3002 | 2 | AI | 4~20mA | [6 empty] | 0 | 100 | %
44 | O1 | 44-ZC-0201 | 44-WCV-0201 | 44-WCV-01 Opening Control Signal | 44-TLA-002 | 22E20-C01-P1-PID-3002 | 2 | AO | 4~20mA | [6 empty] | 0 | 100 | %
45 | O1 | 44-ZLH-002 | 44-TLA-002 | 44-TLA-002 Truck Loading Arm Parked | 44-TLA-002 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact |  | Parked
46 | O1 | 44-ZLL-002 | 44-TLA-002 | 44-TLA-002 Truck Loading Arm Extended | 44-TLA-002 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact |  | Extended
47 | O1 | 44-ED-0001 | 44-ED-0001 | 44-TLB-001 Grouding Unit | 44-TLB-001 | 22E20-C01-P1-PID-4001 | 2 | DI | Dry Contact | Normal | Grounding Fault
48 | O1 | 44-AVA-0001 | 44-AVA-0001 | 44-TLB-001 Audible & Visual Alarm | 44-TLB-001 | 22E20-C01-P1-PID-4001 | 2 | DO | Dry Contact |  | Alarm
52 | A | 04-FCV-0601 | 04-FCV-0601 | PL-0417-4"-150A1 | PL-0417-4"-150A1 | 24E11-P1-PI-1006
53 | A | 04ZC0601 | 04-ZC-0601 | 04-FCV-0601 Opening Control | PL-0417-4"-150A1 | 24E11-P1-PI-1006 |  | AO | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | %
54 | A | 04ZI0601 | 04-ZT-0601 | 04-FCV-0601 Opening Position Feedback | PL-0417-4"-150A1 | 24E11-P1-PI-1006 |  | AI | 4~20mA | Loop Powered | - | - |  |  |  |  | 0 | 100 | %
55 | A | 04-MOV-0201 | 04-MOV-0201 | TLA-402 | 04-MOV-0201 | 24E11-P1-PI-1005
56 | A | 04ZLL0201 | 04-ZSL-0201 | 04-MOV-0201 Fully Closed | 04-MOV-0201 | 24E11-P1-PI-1005 |  | DI | Dry Contact | - | - | Closed |  |  |  |  | 0 | 100 | %
57 | A | 04ZLH0201 | 04-ZSH-0201 | 04-MOV-0201 Fully Open | 04-MOV-0201 | 24E11-P1-PI-1005 |  | DI | Dry Contact | - | - | Open |  |  |  |  | 0 | 100 | %
58 | A | 04XS0201 | 04-HS-0201 | Local/Remote/Off Switch | 04-MOV-0201 | 24E11-P1-PI-1005 |  | DI | Dry Contact | - | Remote | Local/Off |  |  |  |  | 0 | 100 | %
59 | A | 04HSC0201 | 04-MOV-0201 | 04-MOV-0201 Close Command | 04-MOV-0201 | 24E11-P1-PI-1005 |  | DO | Dry Contact | - | - | Open |  |  |  |  | 0 | 100 | %
60 | A | 04HSO0201 | 04-MOV-0201 | 04-MOV-0201 Open Command | 04-MOV-0201 | 24E11-P1-PI-1005 |  | DO | Dry Contact | - | - | Close |  |  |  |  | 0 | 100 | %
61 | A | 04ZI0201 | 04-ZT-0201 | 04-MOV-0201 Opening Position Feedback | 04-MOV-0201 | 24E11-P1-PI-1005 |  | AI | 4~20mA | - | - | - |  |  |  |  | 0 | 100 | %
62 | A | P-101 | P-101 |  | P-101 | 24E11-P1-PI-1004 | 0
63 | A | 01HS0001A | 01-HS-0001A | Remote/Off/Local Switch | P-101 | 24E11-P1-PI-1004 | 0 | DI | Dry Contact | - | Remote | Local/Off
64 | A | 01HS0001B | 01-HS-0001B | Start/Stop Switch | P-101 | 24E11-P1-PI-1004 | 0 | DI | Dry Contact | - | Stop | Start
65 | A | 01HS0001C | 01-HS-0001C | Running/Trip | P-101 | 24E11-P1-PI-1004 | 0 | DI | Dry Contact | - | Trip | Running
66 | A | 01SC0001 | 01-SC-0001 | VSD Speed Control | P-101 | 24E11-P1-PI-1004 | 0 | AO | 4~20mA | Loop Powered | - | -
67 | A | 01SI0001 | 01-SC-0001 | VSD Speed Indication | P-101 | 24E11-P1-PI-1004 | 0 | AI | 4~20mA | Loop Powered | - | -
68 | A | P-501 | P-501 |  | P-501 | 24E11-P1-PI-1004 | 0
69 | A | 01ZI0001 | 01-HS-0001A/B | Running Status | P-501 | 24E11-P1-PI-1004 | 0 | DI | Dry Contact | - | - | Running
70 | A | 01ZI0001 | 01-HS-0001A/B | Duty Status | P-501 | 24E11-P1-PI-1004 | 0 | DI | Dry Contact | - | - | Duty
71 | A | 01ZI0001 | 01-HS-0001A/B | Standby Status | P-501 | 24E11-P1-PI-1004 | 0 | DI | Dry Contact | - | - | Standby
72 | A | 01ZI0001 | 01-HS-0001A/B | Trip Status | P-501 | 24E11-P1-PI-1004 | 0 | DI | Dry Contact | - | - | Trip